## Sheet3
0
| System Voltage ( P-P ) | 415 | Volt |  | Linear Load: |  | General Equipments, Heater
| System Voltage ( P-N ) | 230 | Volt |  | Non-Linear Load: |  | UPS,Invertor,Ballast,VFD
| Future Load Expansion | 0% | % | 1
| Average Intermittent Use of Equipment | 0.8 | (0.7 To 1.0) |  | 0.8 | [42 empty] | Fuel Consumption Chart
Total Connected Load on Diesel Generator Set | [10 empty] | Starting Condition |  |  | Running Condition | [10 empty] | 1Ph | 3Ph | Linear |  | Non-Linear |  | Motor |  |  |  | Liner | Non-Linear | Motor | Total Starting Kva | Liner | Non-Linear | Motor | Total Running Kva | [10 empty] | 3.7879
Sr.No | مشخصات تجهیزات | نوع بار | فاز | تعداد | Load |  | Starting P.F | Running P.F | Diversity Factor | Motor Starter | Starting Amp | Starting Kva | Starting Kw | Full Load Kva | Full Load Kw | Full Load Amp | [5 empty] | Kw | Full Load Kva | Starting Kva | Full Load Amp | Full Load Amp | Starting Amp | Starting Amp | Starting Amp | Starting Amp | Starting Amp | Starting Amp | Full Load Amp | Starting Amp | Starting Kva | Starting Kva | Starting Kva |  | Running Kva | Running Kva | Running Kva | [11 empty] | 0.25 Load(Lt/Hr) | 0.50Load(Lt/Hr) | 0.75 Load(Lt/Hr) | Full Load |  | KVA | KW
[5 empty] | Load | Kw/Hp | [10 empty] | RESULTS | [29 empty] | 20 | 0.6 | 0.9 | 1.3 | 1.6 | 25 | 2.2727 | 3.4091 | 4.9242 | 6.0606 | Full Load | 6.3 | 7.875
| چرثقیل شماره یک | Motor | 3Ph | 1 | 46 | Kw | 0.8 | 0.8 | 0.5 | Y-D | 159.9933 | 115 | 92 | 28.75 | 23 | 39.9983 | Starting Kva | 303.125 |  |  |  | 23 | 28.75 | 28.75 | 0 | 39.9983 | 0 | 0 | 0 | 0 | 0 | 159.9933 | 39.9983 | 159.9933 | 0 | 0 | 115 | 115 | 0 | 0 | 28.75 | 28.75 | Linear | Dol | 1Ph |  | 30 | 1.3 | 1.8 | 2.4 | 2.9 | 37.5 | 4.9242 | 6.8182 | 9.0909 | 10.9848 | 3/4 Load | 9.4 | 11.75
| چرثقیل شماره دو | Motor | 3Ph | 1 | 43 | Kw | 0.8 | 0.8 | 0.5 | Y-D | 149.559 | 107.5 | 86 | 26.875 | 21.5 | 37.3897 | Starting Kw | 242.5 |  |  |  | 21.5 | 26.875 | 26.875 | 0 | 37.3897 | 0 | 0 | 0 | 0 | 0 | 149.559 | 37.3897 | 149.559 | 0 | 0 | 107.5 | 107.5 | 0 | 0 | 26.875 | 26.875 | Non-Linear | Y-D | 3Ph |  | 40 | 1.6 | 2.3 | 3.2 | 4.0 | 50 | 6.0606 | 8.7121 | 12.1212 | 15.1515 | 1/2 Load | 12.5 | 15.625
| PUMP | Motor | 3Ph | 1 | 43 | Kw | 0.8 | 0.8 | 0.5 | Auto.Tra. | 112.1692 | 80.625 | 64.5 | 26.875 | 21.5 | 37.3897 | Starting Amp | 421.7215 |  |  |  | 21.5 | 26.875 | 26.875 | 0 | 37.3897 | 0 | 0 | 0 | 0 | 0 | 112.1692 | 37.3897 | 112.1692 | 0 | 0 | 80.625 | 80.625 | 0 | 0 | 26.875 | 26.875 | Motor | Auto.Tra. |  |  | 60 | 1.8 | 2.9 | 3.8 | 4.8 | 75 | 6.8182 | 10.9848 | 14.3939 | 18.1818 | 1/4 Load | 18.7 | 23.375
|  | Motor | 3Ph | [7 empty] | 0 | 0 | 0 | 0 | 0 | #DIV/0! | Running Kva | 82.5 |  |  |  | 0 | 0 | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Kw | Soft. |  |  | 75 | 2.4 | 3.4 | 4.6 | 6.1 | 93.75 | 9.0909 | 12.8788 | 17.4242 | 23.1061 |  | 25 | 31.25
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | Running Kw | 66 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Hp | Freq.Conv |  |  | 100 | 2.6 | 4.1 | 5.8 | 7.4 | 125 | 9.8485 | 15.5303 | 21.9697 | 28.0303 |  | 31.3 | 39.125
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | Running Amp | #DIV/0! |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 125 | 3.1 | 5.0 | 7.1 | 9.1 | 156.25 | 11.7424 | 18.9394 | 26.8939 | 34.4697 |  | 37.5 | 46.875
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | Alternator Details |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 135 | 3.3 | 5.4 | 7.6 | 9.8 | 168.75 | 12.5 | 20.4545 | 28.7879 | 37.1212 |  | 50 | 62.5
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | Voltage (P-N) | 230 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 150 | 3.6 | 5.9 | 8.4 | 10.9 | 187.5 | 13.6364 | 22.3485 | 31.8182 | 41.2879 |  | 62.5 | 78.125
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | Efficiency | 80% |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 175 | 4.1 | 6.8 | 9.7 | 12.7 | 218.75 | 15.5303 | 25.7576 | 36.7424 | 48.1061 |  | 75 | 93.75
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | Engine Overload Capacity | 130% | (Appro 130% To 150%) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 200 | 4.7 | 7.7 | 11.0 | 14.4 | 250 | 17.803 | 29.1667 | 41.6667 | 54.5455 |  | 93.8 | 117.25
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 230 | 5.3 | 8.8 | 12.5 | 16.6 | 287.5 | 20.0758 | 33.3333 | 47.3485 | 62.8788 |  | 100 | 125
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | Required Generator Rating |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 250 | 5.7 | 9.5 | 13.6 | 18.0 | 312.5 | 21.5909 | 35.9848 | 51.5152 | 68.1818 |  | 125 | 156.25
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | Generator KVA | 242.5 | (Select D.G near This Value) |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 300 | 6.8 | 11.3 | 16.1 | 21.5 | 375 | 25.7576 | 42.803 | 60.9848 | 81.4394 |  | 156 | 195
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | Engine KW | 68.64 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 350 | 7.9 | 13.1 | 18.7 | 25.1 | 437.5 | 29.9242 | 49.6212 | 70.8333 | 95.0758 |  | 187 | 233.75
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 66 | 1.3788 | 400 | 8.9 | 14.9 | 21.3 | 28.6 | 500 | 33.7121 | 56.4394 | 80.6818 | 108.3333 |  | 219 | 273.75
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 150 |  | 500 | 11.0 | 18.5 | 26.4 | 35.7 | 625 | 41.6667 | 70.0758 | 100 | 135.2273 |  | 250 | 312.5
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | Calculate D.G Set Efficiency & Unit Rate of Power |  |  | Calculate Approximate Fuel Consumption |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1.5 |  | 600 | 13.2 | 22.0 | 31.5 | 42.8 | 750 | 50 | 83.3333 | 119.3182 | 162.1212 |  | 342 | 427.5
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 99 |  | 750 | 16.3 | 27.4 | 39.3 | 53.4 | 937.5 | 61.7424 | 103.7879 | 148.8636 | 202.2727 |  | 375 | 468.75
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | D.G Size ( Kva ) | 1000 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1000 | 21.6 | 36.4 | 52.1 | 71.1 | 1250 | 81.8182 | 137.8788 | 197.3485 | 269.3182 |  | 438 | 547.5
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | D.G P.F | 0.8 |  | D.G Size (Kva) | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1250 | 26.9 | 45.3 | 65.0 | 88.8 | 1562.5 | 101.8939 | 171.5909 | 246.2121 | 336.3636 |  | 500 | 625
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | D.G Running Hours | 20 |  | D.G P.F | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1500 | 32.2 | 54.3 | 77.8 | 106.5 | 1875 | 121.9697 | 205.6818 | 294.697 | 403.4091 |  | 625 | 781.25
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | Diesel Consumption (Liter) | 1000 |  | D.G Operation | Full Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1750 | 37.5 | 63.2 | 90.7 | 124.2 | 2187.5 | 142.0455 | 239.3939 | 343.5606 | 470.4545 |  | 350 | 437.5
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | KWH Reading of Meter | 10000 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2000 | 42.8 | 72.2 | 103.5 | 141.9 | 2500 | 162.1212 | 273.4848 | 392.0455 | 537.5 |  | 875 | 1093.75
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | M.F of KWH Meter | 1 |  | Required Diesel |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2250 | 48.1 | 81.1 | 116.4 | 159.6 | 2812.5 | 182.197 | 307.197 | 440.9091 | 604.5455 |  | 1000 | 1250
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | Diesel Rate /Liter (Rs) | 40 |  | Liter/Hour | 23.1061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 1125 | 1406.25
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | Efficiency of D.G | 62.5% |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 1250 | 1562.5
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | KWH/Liter (Unit Per Liter) | 10 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 1563 | 1953.75
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | Unit Rate of Power (Rs) | 4 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 23.1061 | 5 |  |  |  | 1875 | 2343.75
[11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 2488 | 3110
[58 empty] | 2500 | 3125
[58 empty] | 2812 | 3515
[58 empty] | 3130 | 3912.5
[58 empty] | 3750 | 4687.5
[58 empty] | 4375 | 5468.75
[58 empty] | 5000 | 6250
1.2533
future
CALCULATE SIZE OF DIESEL GENERATOR SET